**WHERE DOES MY WATER COME FROM?**

The City of Auburn purchases the water from Barrow County Water Authority.

We also have an emergency tap that allows us to receive water from Gwinnett County.

**Drinking water, including bottled water, may reasonably be expected to contain at least small amounts of some contaminants. The presence of contaminants does not necessarily indicate that water poses a health risk. More information about contaminants and potential health effects can be obtained by calling the EPA’s Safe Drinking Water Hotline (1-800-426-4791).**

**IS OUR WATER SYSTEM MEETING OTHER RULES THAT GOVERN OUR OPERATIONS?**

EPD and EPA require us to test our water on a regular basis to ensure its safety. During 2016, we submitted monthly water samples for Bacteriological analysis in accordance with our Operating Permit. All samples tested satisfactory.

When is testing done?

The water for the City of Auburn is tested daily from several sampling points throughout the City to insure quality drinking water.

We test the Chlorine which the state requires us to maintain a .20ppm (parts per million gallons)

We also test Fluoride which the state requires Auburn to maintain below 2.0ppm

and no less than.5ppm

We test PH range a 1 is Acidic and a 10 is Alkaline. We strive to be at a 7 which is neutral.

We test for Bacterial agents thru the EPD lab in Atlanta.

For the month of August 2017

The average Chlorine residual throughout the City has been .90ppm

We have met and exceeded all EPD goals for the city.

The average PH level has been 7.12 which is inside the good range.

The Fluoride average for the City is .78ppm.

The maximum that can be fed into a system is 4.0 ppm the recommended dose is 2.0ppm or less the least amount is .50ppm we have met that overall goal.

We have tested 8 sites through the City for Bacteria and all 8 have come back negative for Bacteria.